System Parameters:

# System connection parameters

grid_connection = 2000      # Grid connection capacity [kW]

solar_connection = 2000     # Solar connection capacity [kW]

battery_capacity = 40000    # Battery capacity [Ah]

battery_voltage = 100       # Battery voltage [V]

diesel_capacity = 2200      # Diesel generator capacity [kW]

# Hydrogen System Parameters

electrolyzer_capacity = 1000  # Max power consumption of the electrolyzer [kW]

fuel_cell_capacity = 800      # Max power generation of the fuel cell [kW]

h2_tank_capacity = 100        # Hydrogen storage tank capacity [kg]

fuel_cell_efficiency_percent = 0.60 # Fuel cell DC electrical efficiency (60%)

# Cost parameters

pv_energy_cost = 2.85               # PV energy cost [INR/kWh]

load_curtail_cost = 50              # Load curtailment penalty [INR/kWh]

battery_om_cost = 6.085             # Battery O&M cost [INR/kWh]

fuel_cell_om_cost = 1.5             # Fuel cell O&M cost [INR/kWh]

electrolyzer_om_cost = 0.5          # Electrolyzer O&M cost [INR/kWh]

fuel_price = 95                             # INR per liter

# CO2 EMISSION PARAMETERS

# All in kg CO2 per kWh of electrical energy

co2_grid_import = 0.716        # Grid import [kg CO2 / kWh]

co2_diesel = 0.9             # Diesel generator [kg CO2 / kWh]

co2_battery_discharge = 0.029  # Battery discharge [kg CO2 / kWh]

co2_pv_used = 0.046            # PV used [kg CO2 / kWh]

co2_fuel_cell = 0.001          # Assume green H2, no direct CO2

co2_electrolyzer = 0.0        # Assume no direct CO2 (electricity emissions counted at source)

# High CO2-equivalent penalty for load curtailment (only used in CO₂ mode)   # NEW

co2_load_curt_penalty = 5.0  # Very large penalty [kg CO2-eq / kWh curtailed]

CO2 Minimisation Optimization

SUMMARY REPORT

Optimization Mode: CO₂ minimization

Optimization Period: 1 day(s)

Time Resolution: 60 minutes

Total Time Steps: 24

LOAD ANALYSIS:

Total Load Demand:     25100.0 kWh

Total Load Curtailed:      0.0 kWh

Total Load Served:     25100.0 kWh (100.0%)

GRID ANALYSIS:

Grid Import:           10912.0 kWh

Grid Export:               0.0 kWh

DIESEL GENERATOR ANALYSIS:

Energy Generated:          0.0 kWh

Fuel Cost:                0.00 INR

BATTERY ANALYSIS:

Energy Charged:         3200.0 kWh

Energy Discharged:      2888.0 kWh

SOLAR ANALYSIS:

Solar Available:       14500.0 kWh

Solar Used:            14500.0 kWh (100.0%)

Solar Curtailed:           0.0 kWh

HYDROGEN SYSTEM ANALYSIS:

Energy to Electrolyzer:      0.0 kWh

Energy from Fuel Cell:       0.0 kWh

Hydrogen Produced:          0.00 kg

Hydrogen Consumed:          0.00 kg

Fuel Cell O&M Cost:         0.00 INR

Round-Trip Efficiency:       0.0%

Effective Conversion:   0.00 kWh/kg

CO₂ EMISSIONS ANALYSIS:

Grid Emissions:         7812.99 kg CO₂

Diesel Emissions:          0.00 kg CO₂

Battery Emissions:        83.75 kg CO₂

PV Emissions:            667.00 kg CO₂

Fuel Cell Emissions:       0.00 kg CO₂

Electrolyzer Emissions:    0.00 kg CO₂

Curtailment Penalty:       0.00 kg CO₂-eq

──────────────────────────────────

TOTAL CO₂ (physical):   8563.74 kg CO₂

TOTAL CO₂ OBJECTIVE:    8563.74 kg CO₂-eq

Emissions per kWh served:   0.3412 kg CO₂/kWh

COST BREAKDOWN (reference only):

Grid Cost:              67807.40 INR

Diesel Fuel Cost:           0.00 INR

Solar Cost:             41325.00 INR

Battery O&M Cost:       17573.48 INR

Fuel Cell O&M Cost:         0.00 INR

Electrolyzer O&M Cost:      0.00 INR

──────────────────────────────────

TOTAL COST:             126705.88 INR

Cost per kWh served:        5.05 INR/kWh

SYSTEM CONFIGURATION:

✓ Grid Connection

✓ Diesel Generator

✓ Battery System

✓ Solar PV

✓ Hydrogen System (Electrolyzer + Fuel Cell)

Weather: Sunny Day

Cost Minimization

SUMMARY REPORT

Optimization Mode: Cost minimization

Optimization Period: 1 day(s)

Time Resolution: 60 minutes

Total Time Steps: 24

LOAD ANALYSIS:

Total Load Demand:     25100.0 kWh

Total Load Curtailed:      0.0 kWh

Total Load Served:     25100.0 kWh (100.0%)

GRID ANALYSIS:

Grid Import:           15822.5 kWh

Grid Export:            4119.2 kWh

DIESEL GENERATOR ANALYSIS:

Energy Generated:          0.0 kWh

Fuel Cost:                0.00 INR

BATTERY ANALYSIS:

Energy Charged:         1684.2 kWh

Energy Discharged:      1520.0 kWh

SOLAR ANALYSIS:

Solar Available:       14500.0 kWh

Solar Used:            14500.0 kWh (100.0%)

Solar Curtailed:           0.0 kWh

HYDROGEN SYSTEM ANALYSIS:

Energy to Electrolyzer:   1738.3 kWh

Energy from Fuel Cell:     799.2 kWh

Hydrogen Produced:         40.00 kg

Hydrogen Consumed:         40.00 kg

Fuel Cell O&M Cost:      1198.80 INR

Round-Trip Efficiency:      46.0%

Effective Conversion:   43.46 kWh/kg

CO₂ EMISSIONS ANALYSIS:

Grid Emissions:        11328.92 kg CO₂

Diesel Emissions:          0.00 kg CO₂

Battery Emissions:        44.08 kg CO₂

PV Emissions:            667.00 kg CO₂

Fuel Cell Emissions:       0.80 kg CO₂

Electrolyzer Emissions:    0.00 kg CO₂

──────────────────────────────────

TOTAL CO₂ (physical):  12040.80 kg CO₂

Emissions per kWh served:   0.4797 kg CO₂/kWh

COST BREAKDOWN (objective):

Grid Cost:              45567.20 INR

Diesel Fuel Cost:           0.00 INR

Solar Cost:             41325.00 INR

Battery O&M Cost:        9249.20 INR

Fuel Cell O&M Cost:      1198.80 INR

Electrolyzer O&M Cost:    869.15 INR

──────────────────────────────────

TOTAL COST:             98209.36 INR

Cost per kWh served:        3.91 INR/kWh

SYSTEM CONFIGURATION:

✓ Grid Connection

✓ Diesel Generator

✓ Battery System

✓ Solar PV

✓ Hydrogen System (Electrolyzer + Fuel Cell)

Weather: Sunny Day